## protocol specification
1. Instantaneous parameters
# | Modbus |  |  |  |  | Content | Remark
| Modbus register address | R/W | Register length | Data Description | Unit
1 | 0100 | R | 2 | INT32(3+3) | V | voltage
2 | 0102 | R | 2 | INT32(2+3) | A | current | forward and reverse
3 | 0104 | R | 2 | INT32(5+0) | W | active power
4 | 0106 | R | 2 | INT32(5+0) | VA | apparent power
5 | 0108 | R | 2 | INT32(5+0) | var | reactive power
6 | 010A | R | 1 | INT16(2+1) | Hz | frequency
7 | 010B | R | 1 | INT16(1+3) | PF | power factor | With CL indication, active power with sign of forward and reverse(modbus)
2. Energy parameters
# | Modbus |  |  |  |  | Content | Remark
|  | R/W |  |  | Unit
1 | 010E | R | 2 | INT32(6+2) | kWh | Total forward active energy
2 | 0110 | R | 2 | INT32(6+2) | kWh | T1 total forward active energy | without tariffs version: T1= Total forward active energy
3 | 0112 | R | 2 | INT32(6+2) | kWh | T2 total forward active energy | without tariffs version: T2=0
4 | 0114 | R | 2 | INT32(6+2) | kWh | T3 total forward active energy | without tariffs version: T3=0
5 | 0116 | R | 2 | INT32(6+2) | kWh | T4 total forward active energy | without tariffs version: T4=0
6 | 0118 | R | 2 | INT32(6+2) | kWh | Total reverse active energy
7 | 011A | R | 2 | INT32(6+2) | kWh | T1 total reverse active energy | without tariffs version: T1=Total reverse active energy
8 | 011C | R | 2 | INT32(6+2) | kWh | T2 total reverse active energy
9 | 011E | R | 2 | INT32(6+2) | kWh | T3 total reverse active energy
10 | 0120 | R | 2 | INT32(6+2) | kWh | T4 total reverse active energy
11 | 0122 | R | 2 | INT32(6+2) | kWh | Total active energy | You can choose (forward), (reverse), (forward+reverse), (forward-reverse) by the synthetic code
12 | 0124 | R | 2 | INT32(6+2) | kWh | T1 total active energy | without tariffs version: T1= Total active energy
13 | 0126 | R | 2 | INT32(6+2) | kWh | T2 total active energy
14 | 0128 | R | 2 | INT32(6+2) | kWh | T3 total active energy
15 | 012A | R | 2 | INT32(6+2) | kWh | T4 total active energy
16 | 012C | R | 2 | INT32(6+2) | kvarh | Total forward reactive energy
17 | 012E | R | 2 | INT32(6+2) | kvarh | T1 total forward reactive energy | without tariffs version: T1=Total forward reactive energy
18 | 0130 | R | 2 | INT32(6+2) | kvarh | T2 total forward reactive energy
19 | 0132 | R | 2 | INT32(6+2) | kvarh | T3 total forward reactive energy
20 | 0134 | R | 2 | INT32(6+2) | kvarh | T4 total forward reactive energy
21 | 0136 | R | 2 | INT32(6+2) | kvarh | Total reverse reactive energy
22 | 0138 | R | 2 | INT32(6+2) | kvarh | T1 total reverse reactive energy | without tariffs version：T1=total reverse reactive energy
23 | 013A | R | 2 | INT32(6+2) | kvarh | T2 total reverse reactive energy
24 | 013C | R | 2 | INT32(6+2) | kvarh | T3 total reverse reactive energy
25 | 013E | R | 2 | INT32(6+2) | kvarh | T4 total reverse reactive energy
26 | 0140 | R | 2 | INT32(6+2) | kvarh | Total reactive energy
27 | 0142 | R | 2 | INT32(6+2) | kvarh | T1 total reactive energy | without tariffs version: T1=total reactive energy
28 | 0144 | R | 2 | INT32(6+2) | kvarh | T2 total reactive energy
29 | 0146 | R | 2 | INT32(6+2) | kvarh | T3 total reactive energy
30 | 0148 | R | 2 | INT32(6+2) | kvarh | T4 total reactive energy
31 | 014A | R | 2 | INT32(6+2) | kvarh | Total reactive energy in the first quadrant
32 | 014C | R | 2 | INT32(6+2) | kvarh | T1 total reactive energy in the first quadrant | without tariffs version: T1=Total reactive energy in the first quadrant
33 | 014E | R | 2 | INT32(6+2) | kvarh | T2 total reactive energy in the first quadrant
34 | 0150 | R | 2 | INT32(6+2) | kvarh | T3 total reactive energy in the first quadrant
35 | 0152 | R | 2 | INT32(6+2) | kvarh | T4 total reactive energy in the first quadrant
36 | 0154 | R | 2 | INT32(6+2) | kvarh | Total reactive energy in the second quadrant
37 | 0156 | R | 2 | INT32(6+2) | kvarh | T1 total reactive energy in the second quadrant | without tariffs version: T1=Total reactive energy in the second quadrant
38 | 0158 | R | 2 | INT32(6+2) | kvarh | T2 total reactive energy in the second quadrant
39 | 015A | R | 2 | INT32(6+2) | kvarh | T3 total reactive energy in the second quadrant
40 | 015C | R | 2 | INT32(6+2) | kvarh | T4 total reactive energy in the second quadrant
41 | 015E | R | 2 | INT32(6+2) | kvarh | Total reactive energyin the third quadrant
42 | 0160 | R | 2 | INT32(6+2) | kvarh | T1 total reactive energy in the third quadrant | without tariffs version: T1=Total reactive energyin the third quadrant
43 | 0162 | R | 2 | INT32(6+2) | kvarh | T2 total reactive energy in the third quadrant
44 | 0164 | R | 2 | INT32(6+2) | kvarh | T3 total reactive energy in the third quadrant
45 | 0166 | R | 2 | INT32(6+2) | kvarh | T4 total reactive energy in the third quadrant
46 | 0168 | R | 2 | INT32(6+2) | kvarh | Total reactive energy in the fourth quadrant
47 | 016A | R | 2 | INT32(6+2) | kvarh | T1 total reactive energy in the fourth quadran | without tariffs version: T1=Total reactive energy in the fourth quadrant
48 | 016C | R | 2 | INT32(6+2) | kvarh | T2 total reactive energy in the fourth quadran
49 | 016E | R | 2 | INT32(6+2) | kvarh | T3 total reactive energy in the fourth quadran
50 | 0170 | R | 2 | INT32(6+2) | kvarh | T4 total reactive energy in the fourth quadran
51 | 0172 | R | 2 | INT32(6+2) | kWh | Resettable total active energy
52 | 0174 | R | 2 | INT32(6+2) | kvarh | Resettable total reactive energy
53 | 0176 | R | 2 | INT32(6+1) | W | forward active demand
54 | 0178 | R | 2 | INT32(6+1) | W | forward maximum active energy demand
55 | 017A | R | 2 | INT32(6+1) | W | reverse active demand
56 | 017C | R | 2 | INT32(6+1) | W | reverse maximum active energy demand
57 | 0180 | R | 2 | INT32(6+1) | var | forward reactive demand
58 | 0182 | R | 2 | INT32(6+1) | var | Forward maximum reactive demand
59 | 0184 | R | 2 | INT32(6+1) | var | reverse reactive demand
60 | 0186 | R | 2 | INT32(6+1) | var | reverse maximum reactive demand
3. Meter parameters
# | Modbus |  |  |  |  | Content | Remark
|  | R/W |  |  | Unit
1 | 1000 | 6 | R.W | 12-bit serial number,the same as xxx ID,it need to use 10h together, hexadecimal , 012345678910H serial number is 012345678910 |  | Serial No.
2 | 1003 | 1 | R.W | 1-247 |  | Modbus ID
3 | 1004 | 1 | R | 101 |  | FW version
4 | 1005 | 1 | R |  |  | HW version
5 | 1006 | 1 | R | XXXX |  | FW Checksum
6 | 1007 | 4 | R.W | 0 year, month, day, week, hour, minute, second, need to use 10 control code to write at one time |  | Time | Only available in OR-WE-526 with tariff version
7 | 100B | 1 | R.W | 0-99 |  | Scrolling time
8 | 100C | 1 | R.W | 6=9600 7=19200 8=38400 9=115200 |  | 485 baud rate
9 | 100D | 1 | R.W | 0=None 1=Odd 2=even |  | 485 check digit
10 | 100E | 1 | R.W | 1=1bit 2=2bit |  | 485 stop bit
11 | 100F | 1 | R.W | 1=total=forward 2=total=reverse 3=total=forward+reverse 4=total=forward-reverse |  | combined code
| 1010 | 1 |  | 0=Interval 1=Slip |  | demand mode
12 | 1011 | 1 | R.W | The unit minute can be set from 1-30, the default is 15 minutes |  | demand cycle
17 | 1012 | 4 | R.W | In bitwise,0 means no display, and need use the 10 control code should to write at one time (8 bytes are used for three-phase, but only 4 bytes are used for single-phase) |  | Cycle display content automatically
| 1016 | 1 | R.W | Can be set to 0000-9999 |  | password setting of the LCD button display
35 | 1018 | 2 | R.W | Meter running time (start calculation when the current is greater than the setting), write 0 clear to 0, need to use 10 control code to write at one time |  | Meter running time | Only available in OR-WE-526 with tariff version
35 | 101A | 2 | R.W | Unit mA(startup current by default, maximum current's 1.2 times) 10 control code is used to write data at one time |  | Timing current value
15 | 2002 | 1 | W | bit12-Resettable total active energy bit13-Resettable total reactive energy |  | Clear energy
16 | 2003 | 1 | W | 0xA5XX bit0=forward active maximum demand bit1=reverse active maximum demand bit2=forward active maximum demand bit3=forward active maximum demand |  | Clear maximum demand
4. Tariffs parameters
# | Modbus
|  | R/W |  |  | Unit
1 | 1700 | R.W | 12 | hhmmNN*8 Requires continuous write operations and Opcode is 10H |  | Time period table 1 | Only available in OR-WE-526 with tariff version
2 | 170C | R.W | 12 |  |  | Time period table 2
3 | 1718 | R.W | 12 |  |  | Time period table 3
4 | 1724 | R.W | 12 |  |  | Time period table 4
5 | 1730 | R.W | 12 |  |  | Time period table 5
6 | 173C | R.W | 12 |  |  | Time period table 6
7 | 1748 | R.W | 12 |  |  | Time period table 7
8 | 1754 | R.W | 12 |  |  | Time period table 8
9 | 1760 | R.W | 12 | MMDDNN*8 |  | Time zone table
10 | 176C | R.W | 21 | MMDDNN*14 |  | Holidays table

## SO function introduction
Combination code (Measurement mode) | SO Output number | SO Output mode | SO output descrption | SO Output LED | Total energy description
Forward only | SO-1 | Active forward | Only output active forward pulse | Only output positive active pulse | Total energy = Forward energy, no sign for energy in communication and display
| SO-2 | Reactive forward | Only output reactive forward pulse
Reverse Only | SO-1 | Active reverse | Only Output active reverse pulse | Output only reverse active pulses | Total energy = reverse energy, with sign for energy in communication and display
| SO-2 | Reactive reverse | Only output reactive reverse pulse
Absolute (Forward+Reverse) | SO-1 | Absolute active | Output absolute value (forward + reverse) active pulse | Output absolute value (Forward + reverse) active pulse | Total energy =Forward+ reverse energy, without sign for energy in communication and display
Only output active forward pulse
| SO-2 | Absolute Reactive | Output absolute value (forward + reverse) reactive pulse
Only Output active reverse pulse
Algebraic Sum (Forward-Inverse) | SO-1 | Absolute active | Output absolute value (forward + reverse) active pulse |  | Total energy =Forward- reverse energy, with sign for energy in communication and display if reverse>Forward
Only output active forward pulse
| SO-2 | Absolute Reactive | Output absolute value (forward + reverse) reactive pulse
Only Output active reverse pulse